Engineering Conclusion

The objective of this project was to evaluate the performance of an 11/0.4 kV industrial electrical distribution system using ETAP through load flow and short-circuit analyses.

The load flow study confirmed that the electrical system operates within acceptable limits under normal operating conditions. The 2 MVA transformer supplies a total system demand of approximately 1.624 MVA, corresponding to approximately 81% transformer loading, indicating that the transformer has sufficient capacity to support the connected loads while maintaining an adequate operating margin.

An initial analysis identified an overload on the low-voltage feeder connecting the transformer to the main distribution bus. This issue was resolved by replacing the feeder with a 3200 A busduct, eliminating the overload condition and improving the overall reliability of the distribution system.

The voltage profile showed that the minimum operating voltage at the 400 V buses was approximately 97.4% of the nominal voltage. Although this is slightly below the preferred design target of 98%, it remains acceptable for this simplified study and is primarily attributable to the transformer impedance.

The short-circuit analysis determined a maximum three-phase fault current of approximately 51.2 kA at the 400 V bus. The study also demonstrated that the connected motors contribute additional fault current during the initial cycles of the fault, increasing the total fault duty on the low-voltage switchgear.

Based on the calculated fault level, a 65 kA interrupting-capacity circuit breaker is recommended for the low-voltage main incomer to ensure adequate interrupting capability with an appropriate engineering margin.

Overall, the study demonstrates the complete workflow of industrial power system analysis using ETAP, including system modeling, load flow analysis, equipment loading assessment, voltage profile evaluation, and short-circuit analysis. The final design satisfies the primary engineering requirements and provides a safe and reliable electrical distribution system for the specified industrial facility.